## P101
James Fisher Nuclear Limited
Unit 14, Bridge End Industrial Estate, Egremont, Cumbria, CA22 2RD |  |  |  |  | EXXXXX |  |  | Sheet 1 of 1
Pump and Line Calculation Sheet |  |  |  |  | REV | DATE | BY | APVD | DATE | BY | APVD
[5 empty] | A | 2019-09-27 | B MULLINER
Document Number:
Mechanical Piped Services
Equipment Label | P101 |  |  |  | Equipment Name |  |  | Solar Heater Pump
Section | Plant Room
Process Service | Solar Water Heater
Fluid | Water |  |  |  | Density |  |  | 985.7 | kg/m3
Operating Temperature | Normal | 55 | °C |  | Viscosity |  |  | 0.0005039 | Pas
| Min | 1 | °C |  | Normal Max Flowrate |  |  | 8.843 | l/s
| Max | 90 | °C |  | Design Max Flowrate |  |  | 9.2852 | l/s
LINE PRESSURE DROP
SUCTION |  |  |  |  | DISCHARGE
Line Size |  |  | 3 | in | Line Size |  |  |  |  | 3 | in
|  |  |  | Units | [6 empty] | Units
Velocity |  | 1.9391 |  | m/s | Velocity |  |  |  | 1.9391 |  | m/s
Friction Loss |  | 0.63891 |  | kPa/m | Friction Loss |  |  |  | 0.63891 |  | kPa/m
Line Length |  | 1 |  | m | Line Length |  |  |  | 100 |  | m
Line & Misc. Losses |  | 3.0011 |  | kPa | Line & Misc. Losses |  |  |  | 83.0582 |  | kPa
Static Head |  | 8 |  | m | Static Head |  |  |  | 8 |  | m
|  | 77.3577 |  | kPa |  |  |  |  | 77.3577 |  | kPa
Upstream Equipment Pressure |  | 600 |  | kPa | Equipment Pressure |  |  |  | 600 |  | kPa
Sub-Total |  | 677.3577 |  | kPa | Sub-Total |  |  |  | 677.3577 |  | kPa
Suction Pressure |  | 674.3566 |  | kPa | Discharge Pressure |  |  |  | 760.4159 |  | kPa
Vapor Pressure |  | 15.761 |  | kPa | Suction Pressure |  |  |  | 674.3566 |  | kPa
NPSHA |  | 658.5956 |  | kPa | Differential Pressure |  |  |  | 86.0593 |  | kPa
|  | 68.1091 |  | m | Pump Head |  |  |  | 8.8999 |  | m
PUMP DATA
Manufacturer |  | Grundfos |  |  | Driver Type |  |  |  | Three-Phase Electrical
Catalogue No. |  | MAGNA1 100-120 F |  |  | Power Supply |  |  |  | 230 |  | V
Max Pump Flow Rate |  | 29 |  | l/s | Seal Type |  |  |  | Gaskets
Differential Pressure |  | 86.0593 |  | kPa | Hydraulic Power |  |  |  | 5.5711 |  | kW
|  | 8.8999 |  | m | Rated Power | [5 empty] | kW
NPSHR |  |  |  | m | Efficiency | [5 empty] | %
Pump Type |  | Circulator Pump |  |  | Casing Design Pressure |  |  |  | 10 |  | bar
No. of Stages |  | Single |  |  | Casing Design Temperature |  |  |  | 110 |  | °C
Impeller Type |  | Closed |  |  | Casing Material |  |  |  | Cast Iron
Mounting |  | Either
SKETCH
NOTES
1.
2.
3.
4.
5.

## P102
James Fisher Nuclear Limited
Unit 14, Bridge End Industrial Estate, Egremont, Cumbria, CA22 2RD |  |  |  |  | EXXXXX |  |  | Sheet 1 of 1
Pump and Line Calculation Sheet |  |  |  |  | REV | DATE | BY | APVD | DATE | BY | APVD
[5 empty] | A | 2019-09-27 | B MULLINER
Document Number:
Mechanical Piped Services
Equipment Label | P102 |  |  |  | Equipment Name |  |  | Central Heating Circulation Pump
Section | Plant Room
Process Service | Central Heating
Fluid | Water |  |  |  | Density |  |  | 980.53 | kg/m3
Operating Temperature | Normal | 65 | °C |  | Viscosity |  |  | 0.000432 | Pas
| Min | 6 | °C |  | Normal Max Flowrate |  |  | 0.36 | l/s
| Max | 80 | °C |  | Design Max Flowrate |  |  | 0.378 | l/s
LINE PRESSURE DROP
SUCTION |  |  |  |  | DISCHARGE
Line Size |  |  | 1 | in | Line Size |  |  |  |  | 1 | in
|  |  |  | Units | [6 empty] | Units
Velocity |  | 0.4561 |  | m/s | Velocity |  |  |  | 0.4561 |  | m/s
Friction Loss |  | 0.14213 |  | kPa/m | Friction Loss |  |  |  | 0.14213 |  | kPa/m
Line Length |  | 1 |  | m | Line Length |  |  |  | 100 |  | m
Line & Misc. Losses |  | 2.5043 |  | kPa | Line & Misc. Losses |  |  |  | 42.6382 |  | kPa
Static Head |  | 4 |  | m | Static Head |  |  |  | 8 |  | m
|  | 38.476 |  | kPa |  |  |  |  | 76.952 |  | kPa
Upstream Equipment Pressure |  | 600 |  | kPa | Equipment Pressure |  |  |  | 600 |  | kPa
Sub-Total |  | 638.476 |  | kPa | Sub-Total |  |  |  | 676.952 |  | kPa
Suction Pressure |  | 635.9717 |  | kPa | Discharge Pressure |  |  |  | 719.5902 |  | kPa
Vapor Pressure |  | 25.042 |  | kPa | Suction Pressure |  |  |  | 635.9717 |  | kPa
NPSHA |  | 610.9297 |  | kPa | Differential Pressure |  |  |  | 83.6185 |  | kPa
|  | 63.5128 |  | m | Pump Head |  |  |  | 8.6931 |  | m
PUMP DATA
Manufacturer |  | Grundfos |  |  | Driver Type |  |  |  | Three-Phase Electrical
Catalogue No. |  | MAGNA1 25-120 (N) |  |  | Power Supply |  |  |  | 230 |  | V
Max Pump Flow Rate |  | 2.6 |  | l/s | Seal Type |  |  |  | Gaskets
Differential Pressure |  | 83.6185 |  | kPa | Hydraulic Power |  |  |  | 0.2268 |  | kW
|  | 8.6931 |  | m | Rated Power | [5 empty] | kW
NPSHR |  |  |  | m | Efficiency | [5 empty] | %
Pump Type |  | Circulator Pump |  |  | Casing Design Pressure |  |  |  | 10 |  | bar
No. of Stages |  | Single |  |  | Casing Design Temperature |  |  |  | 110 |  | °C
Impeller Type |  | Closed |  |  | Casing Material |  |  |  | Cast Iron
Mounting |  | Either
SKETCH
NOTES
1.
2.
3.
4.
5.

## P103
James Fisher Nuclear Limited
Unit 14, Bridge End Industrial Estate, Egremont, Cumbria, CA22 2RD |  |  |  |  | EXXXXX |  |  | Sheet 1 of 1
Pump and Line Calculation Sheet |  |  |  |  | REV | DATE | BY | APVD | DATE | BY | APVD
[5 empty] | A | 2019-09-26 | B MULLINER
Document Number:
Mechanical Piped Services
Equipment Label | P103 |  |  |  | Equipment Name |  |  | Grey Water Pump
Section | Plant Room
Process Service | Cat 5 Cold Water
Fluid | Water |  |  |  | Density |  |  | 999.377 | kg/m3
Operating Temperature | Normal | 13 | °C |  | Viscosity |  |  | 0.0012009 | Pas
| Min | 6 | °C |  | Normal Max Flowrate |  |  | 1.5 | l/s
| Max | 20 | °C |  | Design Max Flowrate |  |  | 1.575 | l/s
LINE PRESSURE DROP
SUCTION |  |  |  |  | DISCHARGE
Line Size |  |  | 2 | in | Line Size |  |  |  |  | 2 | in
|  |  |  | Units | [6 empty] | Units
Velocity |  | 0.74007 |  | m/s | Velocity |  |  |  | 0.74007 |  | m/s
Friction Loss |  | 0.18443 |  | kPa/m | Friction Loss |  |  |  | 0.18443 |  | kPa/m
Line Length |  | 1 |  | m | Line Length |  |  |  | 20 |  | m
Line & Misc. Losses |  | 0.87023 |  | kPa | Line & Misc. Losses |  |  |  | 11.066 |  | kPa
Static Head |  | 0 |  | m | Static Head |  |  |  | 4 |  | m
|  | 0 |  | kPa |  |  |  |  | 39.2156 |  | kPa
Upstream Equipment Pressure |  | 600 |  | kPa | Equipment Pressure |  |  |  | 600 |  | kPa
Sub-Total |  | 600 |  | kPa | Sub-Total |  |  |  | 639.2156 |  | kPa
Suction Pressure |  | 599.1298 |  | kPa | Discharge Pressure |  |  |  | 650.2816 |  | kPa
Vapor Pressure |  | 1.497 |  | kPa | Suction Pressure |  |  |  | 599.1298 |  | kPa
NPSHA |  | 597.6328 |  | kPa | Differential Pressure |  |  |  | 51.1518 |  | kPa
|  | 60.9587 |  | m | Pump Head |  |  |  | 5.2175 |  | m
PUMP DATA
Manufacturer |  | Dutypoint |  |  | Driver Type |  |  |  | Three-Phase Electrical
Catalogue No. |  | VR2-0511-LHM |  |  | Power Supply |  |  |  | 230 |  | V
Max Pump Flow Rate |  | 2.5 |  | l/s | Seal Type |  |  |  | Gaskets
Differential Pressure |  | 51.1518 |  | kPa | Hydraulic Power |  |  |  | 0.945 |  | kW
|  | 5.2175 |  | m | Rated Power |  |  |  | 1.5 |  | kW
NPSHR |  | 1.75 |  | m | Efficiency |  |  |  | 70 |  | %
Pump Type |  | Cold Water Booster Set |  |  | Casing Design Pressure |  |  |  | 10 |  | bar
No. of Stages |  | Twin |  |  | Casing Design Temperature |  |  |  | 40 |  | °C
Impeller Type |  | Closed |  |  | Casing Material |  |  |  | 304SS
Mounting |  | Vertical
SKETCH
NOTES
1.
2.
3.
4.
5.

## P104
James Fisher Nuclear Limited
Unit 14, Bridge End Industrial Estate, Egremont, Cumbria, CA22 2RD |  |  |  |  | EXXXXX |  |  | Sheet 1 of 1
Pump and Line Calculation Sheet |  |  |  |  | REV | DATE | BY | APVD | DATE | BY | APVD
[5 empty] | A | 2019-09-26 | B MULLINER
Document Number:
Mechanical Piped Services
Equipment Label | P104 |  |  |  | Equipment Name |  |  | CWBS
Section | Plant Room
Process Service | Cold Water
Fluid | Water |  |  |  | Density |  |  | 999.377 | kg/m3
Operating Temperature | Normal | 13 | °C |  | Viscosity |  |  | 0.0012009 | Pas
| Min | 6 | °C |  | Normal Max Flowrate |  |  | 3.17 | l/s
| Max | 20 | °C |  | Design Max Flowrate |  |  | 3.3285 | l/s
LINE PRESSURE DROP
SUCTION |  |  |  |  | DISCHARGE
Line Size |  |  | 2.5 | in | Line Size |  |  |  |  | 2.5 | in
|  |  |  | Units | [6 empty] | Units
Velocity |  | 1.0135 |  | m/s | Velocity |  |  |  | 1.0135 |  | m/s
Friction Loss |  | 0.24726 |  | kPa/m | Friction Loss |  |  |  | 0.24726 |  | kPa/m
Line Length |  | 1 |  | m | Line Length |  |  |  | 100 |  | m
Line & Misc. Losses |  | 23.4883 |  | kPa | Line & Misc. Losses |  |  |  | 247.2552 |  | kPa
Static Head |  | 0 |  | m | Static Head |  |  |  | 8 |  | m
|  | 0 |  | kPa |  |  |  |  | 78.4311 |  | kPa
Upstream Equipment Pressure |  | 600 |  | kPa | Equipment Pressure |  |  |  | 600 |  | kPa
Sub-Total |  | 600 |  | kPa | Sub-Total |  |  |  | 678.4311 |  | kPa
Suction Pressure |  | 576.5117 |  | kPa | Discharge Pressure |  |  |  | 925.6863 |  | kPa
Vapor Pressure |  | 1.497 |  | kPa | Suction Pressure |  |  |  | 576.5117 |  | kPa
NPSHA |  | 575.0147 |  | kPa | Differential Pressure |  |  |  | 349.1745 |  | kPa
|  | 58.6517 |  | m | Pump Head |  |  |  | 35.6159 |  | m
PUMP DATA
Manufacturer |  | Dutypoint |  |  | Driver Type |  |  |  | Three-Phase Electrical
Catalogue No. |  | VT2-10-022T |  |  | Power Supply |  |  |  | 400 |  | V
Max Pump Flow Rate |  | 4.5 |  | l/s | Seal Type |  |  |  | Gaskets
Differential Pressure |  | 349.1745 |  | kPa | Hydraulic Power |  |  |  | 1.9971 |  | kW
|  | 35.6159 |  | m | Rated Power |  |  |  | 2.2 |  | kW
NPSHR |  | 3 |  | m | Efficiency |  |  |  | 68 |  | %
Pump Type |  | Cold Water Booster Set |  |  | Casing Design Pressure |  |  |  | 10 |  | bar
No. of Stages |  | Twin |  |  | Casing Design Temperature |  |  |  | 40 |  | °C
Impeller Type |  | Closed |  |  | Casing Material |  |  |  | 304SS
Mounting |  | Vertical
SKETCH
NOTES
1.
2.
3.
4.
5.

## P105
James Fisher Nuclear Limited
Unit 14, Bridge End Industrial Estate, Egremont, Cumbria, CA22 2RD |  |  |  |  | EXXXXX |  |  | Sheet 1 of 1
Pump and Line Calculation Sheet |  |  |  |  | REV | DATE | BY | APVD | DATE | BY | APVD
[5 empty] | A | 2019-09-26 | B MULLINER
Document Number:
Mechanical Piped Services
Equipment Label | P105 |  |  |  | Equipment Name |  |  | Grey Water Pump
Section | Plant Room
Process Service | Grey Water Supply
Fluid | Water |  |  |  | Density |  |  | 999.377 | kg/m3
Operating Temperature | Normal | 13 | °C |  | Viscosity |  |  | 0.0012009 | Pas
| Min | 6 | °C |  | Normal Max Flowrate |  |  | 1.5 | l/s
| Max | 20 | °C |  | Design Max Flowrate |  |  | 1.575 | l/s
LINE PRESSURE DROP
SUCTION |  |  |  |  | DISCHARGE
Line Size |  |  | 2 | in | Line Size |  |  |  |  | 2 | in
|  |  |  | Units | [6 empty] | Units
Velocity |  | 0.74007 |  | m/s | Velocity |  |  |  | 0.74007 |  | m/s
Friction Loss |  | 0.18443 |  | kPa/m | Friction Loss |  |  |  | 0.18443 |  | kPa/m
Line Length |  | 1 |  | m | Line Length |  |  |  | 100 |  | m
Line & Misc. Losses |  | 0.87023 |  | kPa | Line & Misc. Losses |  |  |  | 184.4341 |  | kPa
Static Head |  | 0 |  | m | Static Head |  |  |  | 8 |  | m
|  | 0 |  | kPa |  |  |  |  | 78.4311 |  | kPa
Upstream Equipment Pressure |  | 600 |  | kPa | Equipment Pressure |  |  |  | 600 |  | kPa
Sub-Total |  | 600 |  | kPa | Sub-Total |  |  |  | 678.4311 |  | kPa
Suction Pressure |  | 599.1298 |  | kPa | Discharge Pressure |  |  |  | 862.8652 |  | kPa
Vapor Pressure |  | 1.497 |  | kPa | Suction Pressure |  |  |  | 599.1298 |  | kPa
NPSHA |  | 597.6328 |  | kPa | Differential Pressure |  |  |  | 263.7354 |  | kPa
|  | 60.9587 |  | m | Pump Head |  |  |  | 26.9011 |  | m
PUMP DATA
Manufacturer |  | Dutypoint |  |  | Driver Type |  |  |  | Three-Phase Electrical
Catalogue No. |  | VR2-0511-LHM |  |  | Power Supply |  |  |  | 230 |  | V
Max Pump Flow Rate |  | 2.5 |  | l/s | Seal Type |  |  |  | Gaskets
Differential Pressure |  | 263.7354 |  | kPa | Hydraulic Power |  |  |  | 0.945 |  | kW
|  | 26.9011 |  | m | Rated Power |  |  |  | 1.5 |  | kW
NPSHR |  | 1.75 |  | m | Efficiency |  |  |  | 70 |  | %
Pump Type |  | Cold Water Booster Set |  |  | Casing Design Pressure |  |  |  | 10 |  | bar
No. of Stages |  | Twin |  |  | Casing Design Temperature |  |  |  | 40 |  | °C
Impeller Type |  | Closed |  |  | Casing Material |  |  |  | 304SS
Mounting |  | Vertical
SKETCH
NOTES
1.
2.
3.
4.
5.

## 50-1HS01-DW-1,2,3
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try:
50-1HS01-DW-1 | 4.4494 | 2.354 | 1.1123 |  | Best option.
Closest NPS (") | 4.5 | 2.5 | 1.5 | 2
Pipe Thickness (Sch 40) (") | 0.247 | 0.203 | 0.145 | 0.154
Reynolds Number | 12795.1454 | 23031.2617 | 38385.4362 | 28789.0771
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.010261 | 0.0031669 | 0.0011401 | 0.0020268
Fluid Velocity (m/s) | 0.14619 | 0.47365 | 1.3157 | 0.74007
Relative Roughness (mm) | 0.00040245 | 0.00072441 | 0.0012073 | 0.00090551
Darcy Friction Factor | 0.028963 | 0.025036 | 0.022276 | 0.023759
Fanning Friction Factor | 0.0072408 | 0.0062589 | 0.005569 | 0.0059397
Frictional Pressure Loss (kPa/m) | 0.003899 | 0.063683 | 0.7287 | 0.18443

## 50-2HS01-SW-4
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try: | Try: | Note: Assume need for 1.5l/s for minimum acceptable flowrate.
50-2HS01-SW-4 | 4.4494 | 2.354 | 1.1123
Closest NPS (") | 4.5 | 2.5 | 1.25 | 1.5 | 2
Pipe Thickness (Sch 40) (") | 0.247 | 0.203 | 0.14 | 0.109 | 0.113
Reynolds Number | 12795.1454 | 23031.2617 | 46062.5234 | 38385.4362 | 28789.0771
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.010261 | 0.0031669 | 0.00079173 | 0.0011401 | 0.0020268
Fluid Velocity (m/s) | 0.14619 | 0.47365 | 1.8946 | 1.3157 | 0.74007
Relative Roughness (mm) | 0.00040245 | 0.00072441 | 0.0014488 | 0.0012073 | 0.00090551
Darcy Friction Factor | 0.028963 | 0.025035 | 0.021435 | 0.022276 | 0.023759
Fanning Friction Factor | 0.0072408 | 0.0062587 | 0.0053588 | 0.005569 | 0.0059397
Frictional Pressure Loss (kPa/m) | 0.003899 | 0.063681 | 1.7448 | 0.7287 | 0.18443

## 65-10HS01-DW-5
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try: | Try:
65-2HS01-DW-5 | 6.5086 | 3.4174 | 1.6272
Closest NPS (") | 7 | 3.5 | 2 | 2.5 | 3
Pipe Thickness (Sch 40) (") | 0.301 | 0.226 | 0.154 | 0.203 | 0.216
Reynolds Number | 17601.1262 | 35202.2524 | 61603.9418 | 49283.1534 | 41069.2945
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.024829 | 0.0062072 | 0.0020268 | 0.0031669 | 0.0045604
Fluid Velocity (m/s) | 0.12928 | 0.5171 | 1.5836 | 1.0135 | 0.70384
Relative Roughness (mm) | 0.00025872 | 0.00051744 | 0.00090551 | 0.00072441 | 0.00060367
Darcy Friction Factor | 0.027042 | 0.022898 | 0.020235 | 0.021228 | 0.022107
Fanning Friction Factor | 0.0067605 | 0.0057244 | 0.0050587 | 0.0053071 | 0.0055268
Frictional Pressure Loss (kPa/m) | 0.0018301 | 0.049588 | 0.71925 | 0.24726 | 0.10348

## 50-10HS01-RW-6
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try: | Try: | Note: Assume need for 1.5l/s for minimum acceptable flowrate.
50-10HS01-RW-6 | 4.4494 | 2.354 | 1.1123
Closest NPS (") | 4.5 | 2.5 | 1.25 | 1.5 | 2
Pipe Thickness (Sch 40) (") | 0.247 | 0.203 | 0.14 | 0.109 | 0.113
Reynolds Number | 12795.1454 | 23031.2617 | 46062.5234 | 38385.4362 | 28789.0771
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.010261 | 0.0031669 | 0.00079173 | 0.0011401 | 0.0020268
Fluid Velocity (m/s) | 0.14619 | 0.47365 | 1.8946 | 1.3157 | 0.74007
Relative Roughness (mm) | 0.00040245 | 0.00072441 | 0.0014488 | 0.0012073 | 0.00090551
Darcy Friction Factor | 0.028963 | 0.025035 | 0.021435 | 0.022276 | 0.023759
Fanning Friction Factor | 0.0072408 | 0.0062587 | 0.0053588 | 0.005569 | 0.0059397
Frictional Pressure Loss (kPa/m) | 0.003899 | 0.063681 | 1.7448 | 0.7287 | 0.18443

## 50-2HS01-SW-7
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try: | Try:
50-2HS01-SW-7 | 4.6953 | 2.4815 | 1.1738
Closest NPS (") | 6 | 3 | 1.5 | 2 | 2.5
Pipe Thickness (Sch 40) (") | 0.28 | 0.216 | 0.145 | 0.154 | 0.203
Reynolds Number | 10686.5054 | 21373.0109 | 42746.0218 | 32059.5163 | 25647.6131
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.018241 | 0.0045604 | 0.0011401 | 0.0020268 | 0.0031669
Fluid Velocity (m/s) | 0.091572 | 0.36629 | 1.4651 | 0.82414 | 0.52745
Relative Roughness (mm) | 0.00030184 | 0.00060367 | 0.0012073 | 0.00090551 | 0.00072441
Darcy Friction Factor | 0.027732 | 0.023444 | 0.020145 | 0.021399 | 0.022485
Fanning Friction Factor | 0.0069331 | 0.005861 | 0.0050362 | 0.0053497 | 0.0056212
Frictional Pressure Loss (kPa/m) | 0.0010986 | 0.02972 | 0.81721 | 0.206 | 0.070927

## 150-2HS01-WW-8
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min |  |  | NOTE: LARGE DIAMETER NEEDED DUE TO SOLIDS, VELOCITY WILL BE INCREASED BY GRAVITY
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try: | Try:
150-2HS01-WW-8 | 6.7846 | 3.5594 | 1.6962
Closest NPS (") | 7 | 3.5 | 2 | 6 | 5
Pipe Thickness (Sch 40) (") | 0.301 | 0.226 | 0.154 | 0.28 | 0.258
Reynolds Number | 19125.5476 | 38251.0952 | 66939.4166 | 22313.1389 | 26775.7667
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.024829 | 0.0062072 | 0.0020268 | 0.018241 | 0.012668
Fluid Velocity (m/s) | 0.14047 | 0.56189 | 1.7208 | 0.1912 | 0.27533
Relative Roughness (mm) | 0.00025872 | 0.00051744 | 0.00090551 | 0.00030184 | 0.0003622
Darcy Friction Factor | 0.026463 | 0.022442 | 0.019858 | 0.025481 | 0.024388
Fanning Friction Factor | 0.0066157 | 0.0056106 | 0.0049646 | 0.0063704 | 0.006097
Frictional Pressure Loss (kPa/m) | 0.0021146 | 0.057386 | 0.83343 | 0.0044009 | 0.010481

## 65-10HS01-DW-9
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try: | Try:
65-2HS01-DW-9 | 6.2914 | 3.3056 | 1.5728
Closest NPS (") | 7 | 3.5 | 2 | 2.5 | 3
Pipe Thickness (Sch 40) (") | 0.301 | 0.226 | 0.154 | 0.203 | 0.216
Reynolds Number | 16445.6089 | 32891.2177 | 57559.631 | 46047.7048 | 38373.0874
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.024829 | 0.0062072 | 0.0020268 | 0.0031669 | 0.0045604
Fluid Velocity (m/s) | 0.12079 | 0.48316 | 1.4797 | 0.94699 | 0.65763
Relative Roughness (mm) | 0.00025872 | 0.00051744 | 0.00090551 | 0.00072441 | 0.00060367
Darcy Friction Factor | 0.027052 | 0.022905 | 0.020242 | 0.021236 | 0.022115
Fanning Friction Factor | 0.006763 | 0.0057264 | 0.0050604 | 0.0053089 | 0.0055287
Frictional Pressure Loss (kPa/m) | 0.0015983 | 0.043306 | 0.62812 | 0.21593 | 0.09037

## 80-10HS01-PW-11
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q
80-10HS01-PW-11 | 10.8033 | 5.6152 | 2.7008 | Note: Minimise pressure drop and diameter but not at the expense of high velocity/dp
Closest NPS (") | 12 | 6 | 3
Pipe Thickness (Sch 40) (") | 0.375 | 0.28 | 0.216
Reynolds Number | 28286.9424 | 56573.8848 | 113147.7695
Flow Type | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.072966 | 0.018241 | 0.0045604
Fluid Velocity (m/s) | 0.12119 | 0.48478 | 1.9391
Relative Roughness (mm) | 0.00015092 | 0.00030184 | 0.00060367
Darcy Friction Factor | 0.023811 | 0.020334 | 0.017983
Fanning Friction Factor | 0.0059528 | 0.0050835 | 0.0044957
Frictional Pressure Loss (kPa/m) | 0.00082616 | 0.022576 | 0.63891

## 25-10HS01-SW-13
Equation | Oil Refining Simple Method | Correlation (304SS, 2006) | NPS for non-viscous flow equation, Q<=100 gal/min
| dioptimum = Q(gpm)^0.5 | dioptimum = 0.55G^0.49 ρ^-0.35 | d=0.25√Q | Try:
25-10HS01-SW-13 | 2.1831 | 1.1716 | 0.54578
Closest NPS (") | 2.5 | 1.25 | 0.75 | 1 | Note: Seek to minimise pressure drop
Pipe Thickness (Sch 40) (") | 0.203 | 0.145 | 0.113 | 0.133
Reynolds Number | 5544.563 | 11089.126 | 18481.8767 | 13861.4075
Flow Type | Turbulent | Turbulent | Turbulent | Turbulent
Cross Sectional Area (m^2) | 0.0031669 | 0.00079173 | 0.00028502 | 0.00050671
Fluid Velocity (m/s) | 0.11403 | 0.4561 | 1.267 | 0.71266
Relative Roughness (mm) | 0.00072441 | 0.0014488 | 0.0024147 | 0.001811
Darcy Friction Factor | 0.036317 | 0.030127 | 0.026656 | 0.028498
Fanning Friction Factor | 0.0090793 | 0.0075318 | 0.006664 | 0.0071246
Frictional Pressure Loss (kPa/m) | 0.005354 | 0.14213 | 1.6172 | 0.41028

## Max Supply Req. Calculations
Cold Water |  |  |  | Cat 5 Cold Water |  |  |  | Hot Water |  |  |  | Grey Water |  |  |  | Grey Water Return |  |  |  | Assumptions:
Furniture | Peak Usage (l/s) | Number | Total Max Usage (l/s) | Furniture | Peak Usage (l/s) | Number | Total Max Usage (l/s) | Furniture | Peak Usage (l/s) | Number | Total Max Usage (l/s) | Furniture | Peak Usage (l/s) | Number | Total Max Usage (l/s) | Furniture | Peak Usage (l/s) | Number | Total Max Usage (l/s) | COTS water efficient equipment is used.
Shower | 0.12 | 23 | 2.76 | Kennel Washing Machine | 0.01 | 1 | 0.01 | Shower | 0.12 | 23 | 2.76 | Toilet | 0.01 | 16 | 0.16 | Shower | 0.01 | 16 | 0.16 | 5 minute shower.
Tap | 0.1 | 23 | 2.3 | Kennel Tap | 0.1 | 1 | 0.1 | Tap | 0.1 | 16 | 1.6 |  |  |  |  | Tap | 0.1 | 16 | 1.6 | Usage taken at peak flow.
Water Cooler | 0.001 | 3 | 0.003 | Kennel Boiler | 0.001 | 1 | 0.001 | [12 empty] | 5% margin of error.
Urinals | 0.01 | 6 | 0.06
Tea Boiler | 0.001 | 2 | 0.002 | [16 empty] | Pipes designed for 20% above max.
[20 empty] | Absolute roughness | 0.046 | mm
Σqn |  |  | 5.125 | Σqn |  |  | 0.111 | Σqn |  |  | 4.36 | Σqn |  |  | 0.16 | Σqn |  |  | 1.76
qnl |  |  | 2.76 | qnl |  |  | 0.1 | qnl |  |  | 2.76 | qnl |  |  | 0.16 | qnl |  |  | 1.6
qet |  |  | 3.2098 | qet |  |  | 0.11799 | qet |  |  | 2.999 | qet |  |  | 0.16 | qet |  |  | 1.6704
Total | Cold+hot+cat 5 |  | 6.3268 | Storage time | (mins) |  | 15 | Storage time | (mins) |  | 15 | Storage time | (mins) |  | 15 | Storage time | (mins) |  | 15
Storage time | (mins) |  | 15
total |  |  | 5978.8124 | Total required storage (l) |  |  | 111.505 | Total required storage (l) |  |  | 2834.088 | Total required storage (l) |  |  | 151.2
|  |  |  | Total Max Potential Supply | 3407.4295 | l |  |  | 100 |  | 13500
|  |  |  | Incoming Flowrate | 1.5 | l/s |  |  | 45 |  | 14850
[9 empty] | 3 |  | So 15000l
Black Water | 3.4878 | [9 empty] | 3516 | 1.9533 | l/s
[11 empty] | 538.8856 | kW
[11 empty] | 7735.2 | l/h
[11 empty] | 8000 | l
[14 empty] | 0.016667 | 8.843 | l/s
[9 empty] | 56.523 | m | 1591.7442 | m^2
[9 empty] | 28.161 | m
Assume 1/3 usable
[11 empty] | 530.5814 | m^2

## Calorifier Calcs
T1 | 6 | °C | (Min expected) | Capacity: | 1450 | l | each
T2 | 65 | °C |  | c | 4.2 | kJ/kg
|  |  |  | Max output | 61.2 | kW | @ | 0.5 | l/s |  | Assume each radiator requires 3kW
Q | 247.8 | kJ/kg°C | [10 empty] | 0.36111
3
0.14118
0.24697

## Miscellaneous Pressure Losses
Fitting or Valve |  | Number of Equivalent Pipe Diameters |  | Total | 366 |  | 18 |  | 93
45° standard elbow |  |  | 15 |  | 23.241 | m | 0.6858 | m | 2.3622 | m
45° long radius elbow |  |  | 10 |  | 5 |  | 4 |  | 13
90° standard radius elbow |  |  | 35
90° standard long elbow |  |  | 23
90° square elbow |  |  | 75
Tee-entry from leg |  |  | 60
Tee-entry into leg |  |  | 90
Union and coupling |  |  | 2
Sharp reduction (tank outlet) |  |  | 25
Sudden expansion (tank inlet) |  |  | 50
Gate valve:
| fully open |  | 7.5
| 1/4 open |  | 800
| 1/2 open |  | 200
| 3/4 open |  | 40
Globe valve, bevel seat:
| fully open |  | 300
| 1/2 open |  | 450
Globe valve, plug disk:
| fully open |  | 450
| 1/2 open |  | 1800
| 1/4 open |  | 5600
Plug valve, open: |  |  | 18